{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["XZV ","XZV  (2)"],"not_rendered":{"images":2,"comments":3},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"XZV ","index":0,"n_rows":51,"n_cols":34,"rows_kept":51,"merged":[[0,1,4,9],[0,10,0,21],[0,22,0,25],[0,26,0,33],[1,22,1,25],[1,26,1,33],[2,22,2,25],[2,26,2,33],[3,10,3,12],[3,13,4,21],[3,22,3,24],[3,25,4,27],[4,10,4,12],[4,22,4,24],[4,28,4,33],[5,1,5,12],[5,13,5,19],[5,20,5,26],[5,27,5,33],[6,1,7,12],[6,13,6,19],[6,20,6,26],[6,27,6,33],[7,13,7,19],[7,20,7,26],[7,27,7,33],[8,1,8,12],[8,13,8,19],[8,20,8,26],[8,27,8,33],[9,1,9,12],[9,13,9,19],[9,20,9,26],[9,27,9,33],[10,1,10,12],[10,13,10,19],[10,20,10,26],[10,27,10,33],[11,1,11,12],[11,13,11,19],[11,20,11,26],[11,27,11,33],[13,1,13,12],[13,13,13,19],[13,20,13,26],[13,27,13,33],[14,1,14,12],[14,13,14,19],[14,20,14,26],[14,27,14,33],[15,1,15,12],[15,13,15,19],[15,20,15,26],[15,27,15,33],[16,1,16,12],[16,13,16,19],[16,20,16,26],[16,27,16,33],[17,1,17,12],[17,13,17,19],[17,20,17,26],[17,27,17,33],[19,1,19,12],[19,13,19,19],[19,20,19,26],[19,27,19,33],[20,1,20,12],[20,13,20,19],[20,20,20,26],[20,27,20,33],[21,1,21,12],[21,13,21,19],[21,20,21,26],[21,27,21,33],[22,1,22,12],[22,13,22,19],[22,20,22,26],[22,27,22,33],[23,1,23,12],[23,13,23,19],[23,20,23,26],[23,27,23,33],[24,1,24,12],[24,13,24,19],[24,20,24,26],[24,27,24,33],[25,1,25,12],[25,13,25,19],[25,20,25,26],[25,27,25,33],[26,13,26,19],[26,20,26,26],[26,27,26,33],[27,1,27,12],[27,13,27,19],[27,20,27,26],[27,27,27,33],[28,1,28,12],[28,13,28,19],[28,20,28,26],[28,27,28,33],[29,1,29,12],[29,13,29,19],[29,20,29,26],[29,27,29,33],[30,1,30,12],[30,13,30,19],[30,20,30,26],[30,27,30,33],[31,1,31,12],[31,13,31,19],[31,20,31,26],[31,27,31,33],[32,1,32,12],[32,13,32,19],[32,20,32,26],[32,27,32,33],[33,1,33,12],[33,13,33,19],[33,20,33,26],[33,27,33,33],[34,1,34,12],[34,13,34,19],[34,20,34,26],[34,27,34,33],[35,1,35,12],[35,13,35,19],[35,20,35,26],[35,27,35,33],[36,1,36,12],[36,13,36,19],[36,20,36,26],[36,27,36,33],[37,1,37,12],[37,13,37,19],[37,20,37,26],[37,27,37,33],[38,1,38,12],[38,13,38,19],[38,20,38,26],[38,27,38,33],[39,1,39,12],[39,13,39,19],[39,20,39,26],[39,27,39,33],[40,1,40,12],[40,13,40,19],[40,20,40,26],[40,27,40,33],[41,1,41,12],[41,13,41,19],[41,20,41,26],[41,27,41,33],[42,1,42,12],[42,13,42,19],[42,20,42,26],[42,27,42,33],[43,1,43,12],[43,13,43,19],[43,20,43,26],[43,27,43,33],[44,1,44,12],[44,13,44,19],[44,20,44,26],[44,27,44,33],[45,1,45,12],[45,13,45,19],[45,20,45,26],[45,27,45,33],[46,1,46,33],[47,1,47,33],[48,1,48,33],[49,1,49,2],[49,3,49,9],[49,10,49,14],[49,15,49,17],[49,18,49,22],[49,23,49,25],[49,26,49,30],[49,31,49,33],[50,1,50,2],[50,3,50,9],[50,10,50,14],[50,15,50,17],[50,18,50,22],[50,23,50,25],[50,26,50,30],[50,31,50,33]],"flags":["formulas_cached_only"]}
[null,"　　　天津渤化工程有限公司\n　　　CHINA TIANJIN BOHUA\n　　　ENGINEERING CO.,LTD.\n(原天津渤海化工集团规划设计院)     ",{"$nulls":8},"仪表数据表\nINSTRUMENT DATA SHEET",{"$nulls":11},"项目名称\nPROJECT",{"$nulls":3},"天津渤海石化有限公司丙烯酸酯和高吸水性树脂新材料项目5万吨/年高吸水性树脂装置项目"]
[{"$nulls":10},"气动切断阀",{"$nulls":11},"项目编号\nPROJ.NO.",{"$nulls":3},"24-101AC-020"]
[{"$nulls":10},"PNEUMATIC SHUTOFF VALVE",{"$nulls":11},"图号 DWG. NO.",{"$nulls":3},"152-IN-03"]
[{"$nulls":10},"子项名称",null,null,"SAP生产厂房-中和单元",{"$nulls":8},"设计阶段",null,null,"施工图",null,null,"第","V1-1","张","共","2","张"]
[{"$nulls":10},"UNIT. NAME",{"$nulls":11}," STAGE",{"$nulls":5}," SHEET          OF "]
[null,"位号 TAG NO.",{"$nulls":11},"XZV-16201",{"$nulls":6},"XZV-16202"]
[null,"用途 SERVICE",{"$nulls":11},"冷冻水回水切断阀",{"$nulls":6},"紧急冷却水回水切断阀"]
[]
[null,"P&ID号 P&ID NO.",{"$nulls":11},"PID-C0385.03-D16",{"$nulls":6},"PID-C0385.03-D16"]
[null,"管道编号 LINE NO.",{"$nulls":11},"LRWR-16201-12\"-A10B-C60",{"$nulls":6},"LRWR-16203-12\"-A10B-C60"]
[null,"管道材质 LINE MATERIAL",{"$nulls":11},"20#",{"$nulls":6},"20#"]
[null,"管道规格 LINE SPECIFICATION",{"$nulls":11},"12\"",{"$nulls":6},"12\""]
[null,"操作条件 OPERATING CONDITIONS"]
[null,"工艺介质 PROCESS FLUID",{"$nulls":11},"急冷水",{"$nulls":6},"急冷水"]
[null,"操作温度 OPER.TEMPER.℃",{"$nulls":11},"-10",{"$nulls":6},"10"]
[null,"操作压力 OPER.PRESSURE MPa(G)",{"$nulls":11},"0.6 MpaG",{"$nulls":6},"0.6 MpaG"]
[null,"最大关闭差压 MAX.DIFF.PRESSURE MPa(G)",{"$nulls":11},"-",{"$nulls":6},"-"]
[null,"正常流量 NOR.FLOW",{"$nulls":11},"920 m3/h",{"$nulls":6},"920 m3/h"]
[null,"阀规格 VALVE SPECIFICATION"]
[null,"型号 MODEL",{"$nulls":11},"-",{"$nulls":6},"-"]
[null,"型式 TYPE",{"$nulls":11},"气动三偏心蝶阀",{"$nulls":6},"气动三偏心蝶阀"]
[null,"公称通径 NOMINAL DIAMETER (mm)",{"$nulls":11},"12\"",{"$nulls":6},"12\""]
[null,"阀体材质 BODY MATERIAL",{"$nulls":11},"304",{"$nulls":6},"304"]
[null,"阀芯材质 PLUG MATERIAL",{"$nulls":11},"304",{"$nulls":6},"304"]
[null,"阀座材质 SEAT MATERIAL",{"$nulls":11},"304",{"$nulls":6},"304"]
[null,"泄漏等级 LEAKAGE CLASS",{"$nulls":11}," ANSI/FCI 70-2 V",{"$nulls":6}," ANSI/FCI 70-2 V"]
[null,"过程连接方式 PROCESS CONN.STYLE",{"$nulls":11},"法兰",{"$nulls":6},"法兰"]
[null,"法兰标准及等级 FLANGE STD.& RATING",{"$nulls":11},"SH/T 3406-2022 class 150",{"$nulls":6},"SH/T 3406-2022 class 150"]
[null,"法兰尺寸及密封面 FLANGE SIZE & FACING",{"$nulls":11},"12\" RF",{"$nulls":6},"12\" RF"]
[null,"执行机构型号 Model",{"$nulls":11},"-",{"$nulls":6},"-"]
[null,"执行机构作用形式 Action type",{"$nulls":11},"双作用(配气包)",{"$nulls":6},"双作用(配气包)"]
[null,"电磁阀型号 SOLENOID MODEL",{"$nulls":11},"两位五通 低功耗",{"$nulls":6},"两位五通 低功耗"]
[null,"防爆等级 EXPOSION-PROOF CLASS",{"$nulls":11},"ExdⅡBT4",{"$nulls":6},"ExdⅡBT4"]
[null,"输入信号 INPUT SIGNAL",{"$nulls":11},"ON/OFF (24V DC)",{"$nulls":6},"ON/OFF (24V DC)"]
[null,"电气接口尺寸 ELEC.CONN.SIZE",{"$nulls":11},"1/2\"NPT(F)",{"$nulls":6},"1/2\"NPT(F)"]
[null,"气源压力 AIR PRESSURE",{"$nulls":11},"0.4MPa",{"$nulls":6},"0.4MPa"]
[null,"气源故障时阀位置 AIR FAIL VALVE POSITION",{"$nulls":11},"FL",{"$nulls":6},"FL"]
[null,"阀位开关 POSITION SWITH",{"$nulls":11},"2个，1 open, 1 close；机械式",{"$nulls":6},"2个，1 open, 1 close；机械式"]
[null,"防爆等级 EXPOSION-PROOF CLASS",{"$nulls":11},"ExdⅡBT4",{"$nulls":6},"ExdⅡBT4"]
[null,"触点形式 CONTACT STYLE",{"$nulls":11},"干接点",{"$nulls":6},"干接点"]
[null,"电气接口尺寸 ELEC.CONN.SIZE",{"$nulls":11},"3/4\"NPT(F)",{"$nulls":6},"3/4\"NPT(F)"]
[null,"过滤减压器 AIR SET",{"$nulls":11},"1/4NPT-Φ8",{"$nulls":6},"1/4NPT-Φ8"]
[null,"气接管尺寸 AIR CONN.SIZE",{"$nulls":11},"Φ8不锈钢管快速接头",{"$nulls":6},"Φ8不锈钢管快速接头"]
[null,"附件 ACCESSORY",{"$nulls":11},"附:过滤减压器",{"$nulls":6},"附:过滤减压器"]
[null,"设计温度/设计压力",{"$nulls":11},"-20 ℃/0.78MPa(G)",{"$nulls":6},"40 ℃/0.78MPa(G)"]
[null,"备注 REMARKS",{"$nulls":11},"全行程关断时间10s;SIL2认证",{"$nulls":6},"全行程关断时间10s;SIL2认证"]
[null,"注：带一体化安装的电涌防护器；所有附件与阀整体安装后成套供货；不锈钢位号牌。电磁阀、过滤减压阀材质为不锈钢。"]
[null,"紧急切断阀为火灾安全型阀门，符合API607或API 6FA标准。易熔塞熔点宜为250℃。"]
[null,"气包具体要求由阀门厂家提供;阀杆材质为304;需要提供TSG证书；"]
[]
[null,"修改\n REV.",null,"说          明  \n DESCRIPTION",{"$nulls":6},"设 计\n DESD.",{"$nulls":4},"日期\nDATE",null,null,"校 核\n CHKD.",{"$nulls":4},"日期\nDATE",null,null,"审 核\n APPD.",{"$nulls":4},"日期\nDATE"]

{"sheet":"XZV  (2)","index":1,"n_rows":51,"n_cols":34,"rows_kept":51,"merged":[[0,1,4,9],[0,10,0,21],[0,22,0,25],[0,26,0,33],[1,22,1,25],[1,26,1,33],[2,22,2,25],[2,26,2,33],[3,10,3,12],[3,13,4,21],[3,22,3,24],[3,25,4,27],[4,10,4,12],[4,22,4,24],[4,28,4,33],[5,1,5,12],[5,13,5,19],[5,20,5,26],[5,27,5,33],[6,1,7,12],[6,13,6,19],[6,20,6,26],[6,27,6,33],[7,13,7,19],[7,20,7,26],[7,27,7,33],[8,1,8,12],[8,13,8,19],[8,20,8,26],[8,27,8,33],[9,1,9,12],[9,13,9,19],[9,20,9,26],[9,27,9,33],[10,1,10,12],[10,13,10,19],[10,20,10,26],[10,27,10,33],[11,1,11,12],[11,13,11,19],[11,20,11,26],[11,27,11,33],[13,1,13,12],[13,13,13,19],[13,20,13,26],[13,27,13,33],[14,1,14,12],[14,13,14,19],[14,20,14,26],[14,27,14,33],[15,1,15,12],[15,13,15,19],[15,20,15,26],[15,27,15,33],[16,1,16,12],[16,13,16,19],[16,20,16,26],[16,27,16,33],[17,1,17,12],[17,13,17,19],[17,20,17,26],[17,27,17,33],[19,1,19,12],[19,13,19,19],[19,20,19,26],[19,27,19,33],[20,1,20,12],[20,13,20,19],[20,20,20,26],[20,27,20,33],[21,1,21,12],[21,13,21,19],[21,20,21,26],[21,27,21,33],[22,1,22,12],[22,13,22,19],[22,20,22,26],[22,27,22,33],[23,1,23,12],[23,13,23,19],[23,20,23,26],[23,27,23,33],[24,1,24,12],[24,13,24,19],[24,20,24,26],[24,27,24,33],[25,1,25,12],[25,13,25,19],[25,20,25,26],[25,27,25,33],[26,13,26,19],[26,20,26,26],[26,27,26,33],[27,1,27,12],[27,13,27,19],[27,20,27,26],[27,27,27,33],[28,1,28,12],[28,13,28,19],[28,20,28,26],[28,27,28,33],[29,1,29,12],[29,13,29,19],[29,20,29,26],[29,27,29,33],[30,1,30,12],[30,13,30,19],[30,20,30,26],[30,27,30,33],[31,1,31,12],[31,13,31,19],[31,20,31,26],[31,27,31,33],[32,1,32,12],[32,13,32,19],[32,20,32,26],[32,27,32,33],[33,1,33,12],[33,13,33,19],[33,20,33,26],[33,27,33,33],[34,1,34,12],[34,13,34,19],[34,20,34,26],[34,27,34,33],[35,1,35,12],[35,13,35,19],[35,20,35,26],[35,27,35,33],[36,1,36,12],[36,13,36,19],[36,20,36,26],[36,27,36,33],[37,1,37,12],[37,13,37,19],[37,20,37,26],[37,27,37,33],[38,1,38,12],[38,13,38,19],[38,20,38,26],[38,27,38,33],[39,1,39,12],[39,13,39,19],[39,20,39,26],[39,27,39,33],[40,1,40,12],[40,13,40,19],[40,20,40,26],[40,27,40,33],[41,1,41,12],[41,13,41,19],[41,20,41,26],[41,27,41,33],[42,1,42,12],[42,13,42,19],[42,20,42,26],[42,27,42,33],[43,1,43,12],[43,13,43,19],[43,20,43,26],[43,27,43,33],[44,1,44,12],[44,13,44,19],[44,20,44,26],[44,27,44,33],[45,1,45,12],[45,13,45,19],[45,20,45,26],[45,27,45,33],[46,1,46,33],[47,1,47,33],[48,1,48,33],[49,1,49,2],[49,3,49,9],[49,10,49,14],[49,15,49,17],[49,18,49,22],[49,23,49,25],[49,26,49,30],[49,31,49,33],[50,1,50,2],[50,3,50,9],[50,10,50,14],[50,15,50,17],[50,18,50,22],[50,23,50,25],[50,26,50,30],[50,31,50,33]],"flags":["formulas_cached_only"]}
[null,"　　　天津渤化工程有限公司\n　　　CHINA TIANJIN BOHUA\n　　　ENGINEERING CO.,LTD.\n(原天津渤海化工集团规划设计院)     ",{"$nulls":8},"仪表数据表\nINSTRUMENT DATA SHEET",{"$nulls":11},"项目名称\nPROJECT",{"$nulls":3},"天津渤海石化有限公司丙烯酸酯和高吸水性树脂新材料项目5万吨/年高吸水性树脂装置项目"]
[{"$nulls":10},"气动切断阀",{"$nulls":11},"项目编号\nPROJ.NO.",{"$nulls":3},"24-101AC-020"]
[{"$nulls":10},"PNEUMATIC SHUTOFF VALVE",{"$nulls":11},"图号 DWG. NO.",{"$nulls":3},"152-IN-03"]
[{"$nulls":10},"子项名称",null,null,"SAP生产厂房-中和单元",{"$nulls":8},"设计阶段",null,null,"施工图",null,null,"第","V1-2","张","共","2","张"]
[{"$nulls":10},"UNIT. NAME",{"$nulls":11}," STAGE",{"$nulls":5}," SHEET          OF "]
[null,"位号 TAG NO.",{"$nulls":11},"XZV-16203",{"$nulls":6},"XZV-16204"]
[null,"用途 SERVICE",{"$nulls":11},"冷冻水上水切断阀",{"$nulls":6},"紧急冷却水上水切断阀"]
[]
[null,"P&ID号 P&ID NO.",{"$nulls":11},"PID-C0385.03-D16",{"$nulls":6},"PID-C0385.03-D16"]
[null,"管道编号 LINE NO.",{"$nulls":11},"LRWS-16201-12\"-A10B-C60",{"$nulls":6},"LRWS-16203-12\"-A10B-C60"]
[null,"管道材质 LINE MATERIAL",{"$nulls":11},"20#",{"$nulls":6},"20#"]
[null,"管道规格 LINE SPECIFICATION",{"$nulls":11},"12\"",{"$nulls":6},"12\""]
[null,"操作条件 OPERATING CONDITIONS"]
[null,"工艺介质 PROCESS FLUID",{"$nulls":11},"急冷水",{"$nulls":6},"急冷水"]
[null,"操作温度 OPER.TEMPER.℃",{"$nulls":11},"-15",{"$nulls":6},"5"]
[null,"操作压力 OPER.PRESSURE MPa(G)",{"$nulls":11},"0.6 MpaG",{"$nulls":6},"0.6 MpaG"]
[null,"最大关闭差压 MAX.DIFF.PRESSURE MPa(G)",{"$nulls":11},"-",{"$nulls":6},"-"]
[null,"正常流量 NOR.FLOW",{"$nulls":11},"920 m3/h",{"$nulls":6},"920 m3/h"]
[null,"阀规格 VALVE SPECIFICATION"]
[null,"型号 MODEL",{"$nulls":11},"-",{"$nulls":6},"-"]
[null,"型式 TYPE",{"$nulls":11},"气动三偏心蝶阀",{"$nulls":6},"气动三偏心蝶阀"]
[null,"公称通径 NOMINAL DIAMETER (mm)",{"$nulls":11},"12\"",{"$nulls":6},"12\""]
[null,"阀体材质 BODY MATERIAL",{"$nulls":11},"304",{"$nulls":6},"304"]
[null,"阀芯材质 PLUG MATERIAL",{"$nulls":11},"304",{"$nulls":6},"304"]
[null,"阀座材质 SEAT MATERIAL",{"$nulls":11},"304",{"$nulls":6},"304"]
[null,"泄漏等级 LEAKAGE CLASS",{"$nulls":11}," ANSI/FCI 70-2 V",{"$nulls":6}," ANSI/FCI 70-2 V"]
[null,"过程连接方式 PROCESS CONN.STYLE",{"$nulls":11},"法兰",{"$nulls":6},"法兰"]
[null,"法兰标准及等级 FLANGE STD.& RATING",{"$nulls":11},"SH/T 3406-2022 class 150",{"$nulls":6},"SH/T 3406-2022 class 150"]
[null,"法兰尺寸及密封面 FLANGE SIZE & FACING",{"$nulls":11},"12\" RF",{"$nulls":6},"12\" RF"]
[null,"执行机构型号 Model",{"$nulls":11},"-",{"$nulls":6},"-"]
[null,"执行机构作用形式 Action type",{"$nulls":11},"双作用(配气包)",{"$nulls":6},"双作用(配气包)"]
[null,"电磁阀型号 SOLENOID MODEL",{"$nulls":11},"两位五通 低功耗",{"$nulls":6},"两位五通 低功耗"]
[null,"防爆等级 EXPOSION-PROOF CLASS",{"$nulls":11},"ExdⅡBT4",{"$nulls":6},"ExdⅡBT4"]
[null,"输入信号 INPUT SIGNAL",{"$nulls":11},"ON/OFF (24V DC)",{"$nulls":6},"ON/OFF (24V DC)"]
[null,"电气接口尺寸 ELEC.CONN.SIZE",{"$nulls":11},"1/2\"NPT(F)",{"$nulls":6},"1/2\"NPT(F)"]
[null,"气源压力 AIR PRESSURE",{"$nulls":11},"0.4MPa",{"$nulls":6},"0.4MPa"]
[null,"气源故障时阀位置 AIR FAIL VALVE POSITION",{"$nulls":11},"FL",{"$nulls":6},"FL"]
[null,"阀位开关 POSITION SWITH",{"$nulls":11},"2个，1 open, 1 close；机械式",{"$nulls":6},"2个，1 open, 1 close；机械式"]
[null,"防爆等级 EXPOSION-PROOF CLASS",{"$nulls":11},"ExdⅡBT4",{"$nulls":6},"ExdⅡBT4"]
[null,"触点形式 CONTACT STYLE",{"$nulls":11},"干接点",{"$nulls":6},"干接点"]
[null,"电气接口尺寸 ELEC.CONN.SIZE",{"$nulls":11},"3/4\"NPT(F)",{"$nulls":6},"3/4\"NPT(F)"]
[null,"过滤减压器 AIR SET",{"$nulls":11},"1/4NPT-Φ8",{"$nulls":6},"1/4NPT-Φ8"]
[null,"气接管尺寸 AIR CONN.SIZE",{"$nulls":11},"Φ8不锈钢管快速接头",{"$nulls":6},"Φ8不锈钢管快速接头"]
[null,"附件 ACCESSORY",{"$nulls":11},"附:过滤减压器",{"$nulls":6},"附:过滤减压器"]
[null,"设计温度/设计压力",{"$nulls":11},"-20 ℃/0.78MPa(G)",{"$nulls":6},"40 ℃/0.78MPa(G)"]
[null,"备注 REMARKS",{"$nulls":11},"全行程关断时间10s;SIL2认证",{"$nulls":6},"全行程关断时间10s;SIL2认证"]
[null,"注：带一体化安装的电涌防护器；所有附件与阀整体安装后成套供货；不锈钢位号牌。电磁阀、过滤减压阀材质为不锈钢。"]
[null,"紧急切断阀为火灾安全型阀门，符合API607或API 6FA标准。易熔塞熔点宜为250℃。"]
[null,"气包具体要求由阀门厂家提供;阀杆材质为304;需要提供TSG证书；"]
[]
[null,"修改\n REV.",null,"说          明  \n DESCRIPTION",{"$nulls":6},"设 计\n DESD.",{"$nulls":4},"日期\nDATE",null,null,"校 核\n CHKD.",{"$nulls":4},"日期\nDATE",null,null,"审 核\n APPD.",{"$nulls":4},"日期\nDATE"]